## Slide 1
Jones Family PV Battery Upgrade Project
February 20, 2023
Topic | Page
Current System | 2
New System Block diagram | 4
Inverter Upgrade | 5
Additional PV Panels | 6
PV Roof Mount System | 9
New Battery Backup System | 10
Conduit | 14
Service Panel Upgrade | 16
Parts List | 17
Appendix A - System Analysis | 18

## Slide 2
Current System
1.8 kW net PV system installed in 2003
12 180W Sharp PV Panels
Inverter location
Keep

## Slide 3
Current System
SMA Sunny Boy 2500W inverter
DC shutoff
AC shutoff
90 amp service panel
Upgrade
Upgrade

## Slide 4
New System Block Diagram
DCDC Chargers
Grid
240V:
  Air and water heat pump (future)
  Level 2 EV charger
  Resistive heat clothes dryer
  Double convection oven
  Stove
120V:
  Level 1 EV charger
  Clothes washer
  Dishwasher
  Lighting
  Kitchen appliances
  Garage tools
  Electronics
  Everything else
Service panel
meter
Inverter Bypass
Switch
240 VAC
48 VDC
500 VDC
CANBus
Legend:
DC/AC Inverter
AC/DC Charger
Control
Grid circuit breaker
All-in-one
12 original PV panels
26 new
PV panels
Battery cell, BMS and contactor box
120 VAC
Load circuit breaker
box

## Slide 5
Inverter Upgrade
Sol-Ark 15K-2P-N All-in-one: https://www.sol-ark.com/sol-ark-15k-all-in-one/
$8,295 through EcoDirect in Carlsbad, CA: more local distributor? https://www.altestore.com/store/inverters/hybrid-inverters/sol-ark-hybrid-inverter-pre-wired-systems-p41381/#SOLARK15K
31.8” high
18.3” wide
10.9” deep
135 lbs
Outdoor rated
Wall mount
WiFi connection
Designed and assembled in Texas
3 PV MPPT inputs:
500V open circuit max
26 amps max per MPPT
2 strings max per MPPT
Lithium battery manager CANBus interface
Battery power interface:
48V nominal
275 amp max
50 to 9900 amp-hours
Grid interface
Load interface:
12 kW max continuous from batteries only
15 kW max continuous using grid

## Slide 6
$318 each from EcoDirect in Carlsbad, CA: more local distributor? https://www.ecodirect.com/Mission-Solar-345-Watt-All-Black-Mono-Solar-Panel-p/mission-solar-mse345sx5t.htm
Additional PV Panels
Mission Solar MSE345SX5T 345 Watt Panels: https://www.missionsolar.com/wp-content/uploads/2022/03/C-SA2-MKTG-0025-Data-Sheet-for-SX5T.pdf
41V open circuit
11A short circuit current
69” high
42” wide
1.6” deep
45 lbs
25 year warranty to 84% capacity
Designed and assembled in Texas

## Slide 7
Additional PV Panels
SE garage roof
SE family room roof (not shown)
SE roof above bedrooms

## Slide 8
Additional PV Panels
Up to 26 fit in mixed orientations x 345W = 8970W in to DC/DC battery charger.

## Slide 9
PV Roof Mount System
Standing seam metal roof installed ~2007, 1” high x ½” wide seam, 17.25” center-to-center
Current array on SW overhang with 2.5/12 pitch; SE side is 5/12
S5! S-5-S mounting system, 1” spacing on ends and between panels

## Slide 10
New Battery Backup System
Up to 8 used 48V 100 amp hour LiFePO4 electric vehicle battery packs in parallel
4 Valence Ucharge XP Modules
16 HiPower Cells

## Slide 11
New Battery Backup System
Insert Trevor’s BMS info and connection to All-in-one here
Add battery box details:
Foundation
Underground conduit
Shell
Rack system

## Slide 12
New Battery Backup System
Battery box location (rose bushes to be transplanted)
Service panel

## Slide 13
New Battery Backup System
Battery box mockup

## Slide 14
Legend
System components
All-in-one
Service Panel
Existing SW-facing PV array
Conduit
Conduit
New PV panels
Batteries w/BMS

## Slide 15
Conduit
TBD
Which wires go in which conduit
Junction boxes
Layout

## Slide 16
Service Panel Upgrade
TBD
Grid circuit breaker
Bypass switch
Load circuit breakers

## Slide 17
Part List fill out
Item No. | Item | Make | Model | Supplier | Unit cost | Qty | Tax | Shipping | Subtotal
1 | All-in-one | Sol-Ark | 15K-2P-N | EcoDirect | $8,295 | 1 |  |  | $8,295++
2 | PV panels | Mission Solar | MSE345SX5T | EcoDirect | $318 | 26 |  |  | $8,268++
3 | Roof panel attachments | S5! | S-5-S |  |  |  |  |  | 
4 | Battery cells | Will start with 2 5 kWh packs I already own |  |  |  |  |  |  | $0
5 | Battery management boards | THJ Media | BMS-1 |  |  |  |  |  | 
6 | Battery box foundation, shell and underground conduit |  |  |  |  |  |  |  | 
7 | Battery box rack | Home made |  |  |  |  |  |  | 
8 | Power wiring |  |  |  |  |  |  |  | 
9 | Control wiring |  |  |  |  |  |  |  | 
10 | Above ground conduit |  |  |  |  |  |  |  | 
11 | Conduit junction boxes |  |  |  |  |  |  |  | 
12 | Grid circuit breaker, inverter bypass switch and load circuit breaker box |  |  |  |  |  |  |  | 
Total |  |  |  |  |  |  |  |  | $16,563++

## Slide 18
Appendix A – System Analysis

## Slide 19
Chart: Electrical Usage Daily since owning long range EV only: average 16.6 kWh, min 10.0 kWh, max 26.5 kWh ~14 kWh in summer, ~19 kWh in winter (boxed), $1,515/yr at $.25/kWh, 6.1 MWh/yr
| 43101 | 43130 | 43160 | 43191 | 43221 | 43251 | 43282 | 43312 | 43342 | 43374 | 43404 | 43436 | 43467 | 43496 | 43528 | 43557 | 43587 | 43619 | 43648 | 43678 | 43711 | 43740 | 43769 | 43802 | 43832 | 43863 | 43893 | 43922 | 43954 | 43984 | 44013 | 44042 | 44074 | 44104 | 44136 | 44167 | 44199 | 44228 | 44258 | 44287 | 44319 | 44349 | 44378 | 44410 | 44440 | 44472 | 44501 | 44532
 | 28.0044 | 26.5322 | 20.304 | 22.3049 | 18.4721 | 18.4389 | 16.3608 | 15.7338 | 10.2513 | 15.073 | 15.0539 | 22.2934 | 23.7755 | 20.6288 | 18.4659 | 15.4412 | 13.0382 | 12.9866 | 12.8153 | 11.0019 | 13.7888 | 11.3928 | 10.8467 | 17.6038 | 17.7067 | 17.8047 | 9.9735 | 13.0524 | 14.7209 | 14.0587 | 13.3575 | 10.562 | 19.5584 | 17.6301 | 13.5623 | 14.2274 | 23.1482 | 15.309 | 23.7524
System Analysis

## Slide 20
Furnace needed Nov-Apr;
April good for solar, Nov bad
Local irradiation
According to NREL, our GHI (Global Horizontal Irradiation) = full sun hours equivalent per year = 1694, in Jan it is 65/31=2.1 hours per day and in May-July it is 225/31=7.3 hours per day. Annual average is 1694/365=4.6 hours per day. Multiply by net PV output to calculate energy produced in kWh per day.
System Analysis
8 kW PVs x 4.6 average full sun hours per day should generate 37 kWh/day average. With enough battery backup to store it for overnight use we would have >2x our current average need.

## Slide 21
Chart: Monthly Natural Gas Usage 9 therms/month for hot water, 108 therms/year; 312 therms/year for furnace 420 therms/year total, $848/year at $2/therm average
System Analysis
But we eventually want to add a high efficiency space and water heat pump that uses most in the winter when we have the least sun, so we need to know the added load and upsize accordingly, possibly curtailing any solar we can’t sell back to the grid in the summer.

## Slide 22
Added heat pump load estimate
We consume an average of 420 therms or 12,306 kWh/year of natural gas for space and water heat. We generally run our heater Nov-Apr where the lows are 39 to 44 F on average, vs. 48 to 52F for the rest of the year. Based on Chiltrix data it looks like COP will be around 2.6 for 122 degree domestic hot water which is assumed to be what will be used for the furnace, so we will need about 4,733 kWh per year, and our energy bills without solar would be about $346 more per year or about $1 per day, not a high price to pay to enable renewably powered heating, only ~1/4 of a Venti latte at Starbucks.
Average temps according to Google:
Heat pump COP according to manufacturer:
System Analysis

## Slide 23
Chart: Estimated new daily electric use
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
added space heat | 25.6082 | 23.4914 | 13.4908 | 6.3442 | 1.5753 | -0.20869 | -0.24235 | 0.28274 | 0.083476 | 1.6561 | 17.8221 | 27.7894
added water heat | 3.2717 | 3.5902 | 3.2717 | 3.3808 | 3.2717 | 3.3808 | 3.2717 | 3.2717 | 3.3808 | 3.2717 | 3.3808 | 3.2717
everything else | 21.2477 | 17.4939 | 16.6142 | 15.6244 | 14.8761 | 14.3748 | 12.4757 | 14.1844 | 17.0445 | 13.4781 | 21.5112 | 20.3508
total | 50.1277 | 44.5755 | 33.3767 | 25.3494 | 19.7231 | 17.5469 | 15.5051 | 17.7389 | 20.5087 | 18.4058 | 42.7141 | 51.4119
System Analysis
Thus future needs will rise once we add a high efficiency heat pump.

## Slide 24
System Analysis
Chart: Overnight Use Solar Battery System Sizing Assumptions: 1.) all energy used when sun is down; 2.) batteries only charged by solar; 3.) add batteries until no improvement
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 34 | 35 | 36 | 37 | 39 | 40 | 41 | 43 | 44 | 45 | 47 | 48 | 49 | 50 | 52 | 53 | 55 | 58 | 61 | 64 | 67 | 70 | 73 | 78 | 85 | 87 | 93
number of batteries | 1 | 3 | 4 | 4 | 5 | 6 | 7 | 8 | 9 | 8 | 9 | 10 | 9 | 10 | 11 | 9 | 10 | 10 | 10 | 10 | 10 | 11 | 12 | 12 | 12 | 13 | 13 | 13 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 16 | 17 | 17 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 20 | 21 | 22
number of Sol-Ark 12ks | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3
energy from batts, % | 5 | 11 | 16 | 21 | 26 | 32 | 36 | 40 | 43 | 45 | 48 | 50 | 51 | 53 | 55 | 56 | 58 | 59 | 60 | 61 | 62 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100
net meter ratio x10 | 0.5 | 1.1 | 1.6 | 2.1 | 2.6 | 3.2 | 3.7 | 4.2 | 4.8 | 5.3 | 5.9 | 6.4 | 7 | 7.6 | 8 | 9.1 | 9.7 | 10.2 | 10.8 | 11.3 | 11.9 | 12.4 | 13 | 13.5 | 14.1 | 14.6 | 15.2 | 15.7 | 16.3 | 16.8 | 17.4 | 18.5 | 19 | 19.6 | 20.1 | 21.2 | 21.8 | 22.4 | 23.5 | 24 | 24.6 | 25.7 | 26.2 | 26.8 | 27.3 | 28.4 | 29 | 30 | 31.7 | 33.4 | 35.1 | 36.7 | 38.4 | 40 | 42.8 | 46.7 | 47.8 | 51.1
cost, k$ | 14.238 | 19.576 | 22.464 | 22.902 | 25.79 | 28.678 | 31.566 | 34.454 | 37.342 | 35.33 | 38.218 | 41.106 | 39.094 | 41.982 | 44.87 | 40.846 | 43.734 | 44.172 | 44.61 | 45.048 | 45.486 | 48.374 | 51.262 | 51.7 | 52.138 | 55.026 | 55.464 | 55.902 | 58.79 | 59.228 | 59.666 | 60.542 | 60.98 | 61.418 | 71.206 | 72.082 | 72.52 | 72.958 | 73.834 | 74.272 | 77.16 | 78.036 | 80.924 | 81.362 | 84.25 | 85.126 | 88.014 | 88.89 | 90.204 | 91.518 | 92.832 | 94.146 | 95.46 | 106.124 | 108.314 | 111.38 | 114.706 | 119.784
extra cost/day, $ | 4.71 | 5.76 | 6.13 | 5.84 | 6.21 | 6.59 | 6.97 | 7.34 | 7.71 | 6.74 | 7.1 | 7.47 | 6.49 | 6.86 | 7.23 | 5.26 | 5.63 | 5.48 | 5.53 | 5.58 | 5.62 | 6.34 | 7.06 | 7.11 | 7.16 | 7.88 | 7.92 | 7.97 | 8.69 | 8.74 | 8.79 | 8.88 | 8.93 | 8.98 | 11.59 | 11.69 | 11.73 | 11.78 | 11.88 | 11.93 | 12.64 | 12.74 | 13.46 | 13.51 | 14.23 | 14.32 | 15.04 | 15.14 | 15.28 | 15.43 | 15.57 | 15.71 | 15.86 | 18.56 | 18.8 | 19.14 | 19.91 | 20.87
It’s hard to go completely off grid. We will target an eventual size of 8 kW generation with 40 kWh production to get about 69% off grid at about ¼ the cost of getting 99% off the grid.

## Slide 25
System Analysis
Estimated future system performance.